All Souls Interfaith Gathering, Inc.

P.O. Box 309

Shelburne, VT 04582

(802) 985-3819

Solid fuel boiler information:

Stoker, Firebox and controls:  Solagen, Inc

Dear Island, Oregon (503) 366-4210

500,000/BTU

Boiler:  Burnham Model 4NW-127A triple pass hot water boiler

Gross Output:  15.6 HP,  522 MBH

Net Rating:  454 MBH

Heating Surface:  Fireside 96 sq. ft., Waterside 100 sq. ft.

Purchased from: Biomass Commodities Corp.

Williamstown, MA 01267

(413) 458-5326

In Service since 12/2007 heating +/- 14,000 sq. ft of space

Low ash pellet consumption rates:  Low fire (75% or operation time) +/- 6 lbs./hour

Hi Fire (25% or operation time) +/- 58 lbs./hour

Operation water loop temperature: 170-180 F

Hi fire firebox temp: 900-1200 F

Hi Fire stack temp: 180 – 280 F

We brush the tubes when stack temp exceeds 350F

Anticipate brushing 3-4 times per season depending on fuel ash content

Start to finish vac and brush tubes : 1 hour

2007-08 consumption:  +/- 40 tons

2008-09 consumption (anticipated): +/- 34 tons

Operator for All Souls: Christopher W. Davis (802) 985-9218

2-25-09